## Steam Cycle (reheat)
| mass feed water | 150 | kg/s |  | η isentropic HP | 0.85
| T after closed preheater LP | 140 | C |  | η isentropic LP | 0.8
| T after closed preheater HP | 280 | C
| Cp water | 4.18 | kJ/ kg K |  | η mechanical | 0.95
[5 empty] | η generator | 0.95
|  | Considering isentropic efficiency (real), |  |  | graph
|  | h1 = | 3350 | kJ/kg | h3 = | 3462.5 | kJ/kg
|  | h2 is = | 2875 | kJ/kg | h4 is = | 2270 | kJ/kg
|  | h2 = | 2946.25 | kJ/kg | h4 = | 2508.5 | kJ/kg
[5 empty] | h5, sat liq 0.05= | 137.5 | kJ/kg
|  | h x = | 3050 | kJ/kg | h6 = | 137.5 | kJ/kg
|  | h y = | 3325 | kJ/kg | h7 = | 585.2 | kJ/kg
|  | h z = | 3025 | kJ/kg | h8, sat liq 10 = | 762.7 | kJ/kg
[5 empty] | h9= | 1170.4 | kJ/kg
Feedwater tank |  |  |  |  | h10, sat liq 30= | 1008.3 | kJ/kg
m tot. h8 = my. Hy + mx h10 + (mtot - mx - my) h7 |  |  |  |  | h11, sat liq 2= | 504.8 | kJ/kg
my = | 5.0923 | kg/s
HP Preheater |  | LP Preheater
m tot (h9-h8)= mx (hx - h10) |  | (mtot - my-mx) (h7-h6) = mz (hz - h11)
mx= | 29.953 | mz = | 20.4211 | kg/s | m tot-my-mx= | 114.9547 | kg/s
Turbine
| From HP | P gross= m tot (h1-hx) + (mtot - mx) (hx-h2)
|  | PT gross HP= | 57454.8783 | kW | 57.4549 | MW
| From LP | P gross = (m tot-mx) (h3-hy) + (mtot-mx-my) (hy-hz) + (m tot-mx-my-mz) (hz-h4)
|  | PT gross LP = | 99819.4987 |  | 99.8195 | MW
|  | P gross total= | 157.2744
| Total | P net = | 141.9401 | MW
P = 165 bar
T = 560 C
m = 200 kg/s
P = 30 bar
T = 560 C
P = 0.15 bar
P = 2 bar
P = 30 bar
T = 140 C
mx
P = 40 bar
my
mz
P = 10 bar
T = 280 C
11
8
9
10

## Steam cycle (extractions)
Data Set Nr | 40 |  | η isentropic | 0.8
AA | 75 |  | η mechanical | 0.98
BB | 10 |  | η generator | 0.97
CC | 10 |  | η thermal | 0.92
ma= | 15 | kg/s | m total= | 120 | kg/s
H.fwt= | 432.5 | kJ/kg
Considering isentropic efficiency (real), |  |  |  |  | graph
h inlet turbine = |  | 3427 | kJ/kg | ha= | 3090 | kJ/kg
h outlet turbine, is = |  | 2370 | kJ/kg | hb= | 2875 | kJ/kg
h outlet turbine real= |  | 2581.4 | kJ/kg | hc= | 2650 | kJ/kg
HP Preheater |  |  |  |  | steam table
m total x (hout pre - ha sat 6) = ma x (ha - ha sat 20) |  |  |  | ha sat (6)= | 670.5 | kJ/kg
h out pre = |  | 943.175 | kJ/kg | ha sat (20)= | 908.6 | kJ/kg
FWT
m total x h sat(6) = mb x hb + ma x h sat (20) + (m total - ma - mb) x h fwt
m b = | 8.7691 | kg/s
steam table
|  |  |  | ha sat (0.8)= | 391.7 | kJ/kg
LP Preheater |  |  |  | ha sat (1.5)= | 467.2 | kJ/kg
(m total - ma-mb) x (h fwt - h sat(0.8)) = mc x (hc - h sat (1.5))
m c = | 1.7987 | kg/s
m fw entering fwt= | 96.2309 | kg/s
Turbine
PT gross= | m total (h in - ha) + (m-ma)(ha-hb) + (m-ma-mb)(hb-hc)+ (m -ma-mb-mc)(hc - h out turbine)
PT gross= | 91145.004 | kW | 91.145 | MW
P net = | 86.6424 | MW
Boiler
Q boiler = | 298059 | kW | 298.059 | MW
Q fuel = | 323977.1739 | kW | 323.9772 | MW
η elec total= | 26.74%

## Steam cycle (backpressure)
Mass superheater (msh) | 1.5 | kg/s | Fuel flow | 0.14 | kg/s |  | Cp water | 4.18 | kJ/kg
|  |  | T increase district water heating | 10 | C |  | Density | 1000 | kg/m3
|  |  | District heating water flow | 4.85 | m3/ min | 80.8333 | kg/s
|  |  | H fuel | 42300 | kJ/kg
| Considering isentropic efficiency (real), |  |  | graph and steam table
| h fw out (sat, 4 bar) = | 604.8 | kJ/kg | Hsh in | 3215 | kJ/kg
| H sat (40 bar steam) | 2801.4 | kJ/kg | h cond out(sat, 1.2 bar) | 439.2 | kJ/kg
Feedwater tank
(msh + msat).hfw out = msh. Hsh out + msat. Hsat
| msat= | 0.11308 | kg/s
| mfw= | 1.6131 | kg/s
Boiler
η boiler. M fuel. Hfuel + (msat + msh). Hfw out = msat. H sat + msh. Hsh in
| η boiler= | 70.31%
Condenser
m Cp water Delta T = msh (h outlet turbine - h cond out)
| h outlet turbine= | 2691.7556 | kJ/kg
Turbine
| h outlet turbine, is | 2480 | kJ/kg
| η isentropic= | 71.19%